S4 Table. Medical Wastewater Monitoring Data.

| Season | COD (mg/L) | Residual chlorine level (mg/L) | Outlet water temperature（℃） |
| --- | --- | --- | --- |
| March | 60.21±13.74 | 2.64±0.26 | 18.53±0.75*** |
| July | 77.52±13.54 | 3.36±1.74 | 28.03±1.23*** |
| October | 60.53±45.16 | 4.34±1.54 | 24.14±2.13*** |
| December | 117.96±35.27 | 2.32±0.37 | 16.3±4.15*** |

COD limit: < 250 mg/L (Secondary Standard for effluent entering municipal networks).

Residual chlorine limit: 2–8 mg/L (measured at the disinfection tank outlet).

Standard ANOVA analysis revealed highly significant differences in mean values among groups, ***p<0.001.